**HOW TO SPECIFY**

**FM Series**

**FLOWLINE LINEAR DIFFUSERS**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install Nailor FlowLine™ modular square ceiling diffusers of the size and type shown on the architectural and mechanical plans and/or air distribution schedules. Diffusers shall be designed as a nominal 24" x 24" (600 x 600mm) module size. Mechanical contractor shall coordinate installation with General Contractor and other sub-contractors as required.These diffusers shall utilize heavy wall extruded aluminum frames with inside and outside mitered corners. The diffusers shall feature a 1" (25) continuous slot around all four sides with dual pattern controllers that are fully adjustable to permit throttling, as required for air volume reduction or complete shut-off without adding any blank-off devices. Diffusers shall be capable of being adjustable for a 4, 3, 2 or 1-way blow pattern as required after installation. Pattern controllers shall be minimum 20 ga. (1.01) corrosion-resistant steel. One-piece pattern controllers are not acceptable. The pattern controllers shall be horizontal high throw type and shall maintain a tight ceiling air pattern from maximum to minimum cataloged airflows and be suitable for VAV systems.Supply units shall be complete with a compatible steel back pan that is removable and secured by steel ‘s’ clips. The back pan shall incorporate an integral drawn round neck to permit hard or flexible duct connection. Return units shall be similar in appearance but feature a light shield back pan for ductless return installations. The center acoustical ceiling tile shall be supplied, cut and field installed by the acoustical tile sub-contractor.Exposed flange/border frames shall be factory painted standard white or custom painted to match specified architectural requirements. Provide paint samples if required. Pattern controllers and integral spacers shall be painted flat black.Performance of the ceiling diffuser shall be based upon cataloged data obtained from tests conducted in accordance with ASHRAE Standard 70-2006. Pattern controllers shall be field adjusted after diffuser installation and set in their normal operating condition. Air test and balancing of ceiling diffusers shall be in accordance with the testing and balancing portion section of the specifications.Provide manufacturers submittal drawings and published performance data. |