**HOW TO SPECIFY**

**Models 51DV(-O), 51DH(-O)**

**ALUMINUM SUPPLY GRILLES AND REGISTERS – DOUBLE DEFLECTION**

|  |
| --- |
| **SUGGESTED SPECIFICATION:****51DV, 51DH Double Deflection**Furnish and install **Nailor Model** (select one) **51DV** or **51DH Double Deflection Supply Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall have a dual set of extruded aluminum adjustable blades that are streamlined shaped and spaced on 3/4" (19) centers. The frame is to be constructed from heavy gauge extruded aluminum and have reinforced mitered corners. The finish shall be AW Appliance White (optional finishes are available).(Optional) An opposed blade damper, constructed of heavy gauge corrosion-resistant steel (aluminum is optional) and operable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2006. |

**Models 51SV(-O), 51SH(-O)**

**ALUMINUM SUPPLY GRILLES AND REGISTERS – SINGLE DEFLECTION**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install **Nailor Model** (select one) **51SV** or **51SH Single Deflection Supply Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall have a single set of extruded aluminum adjustable blades that are streamlined shaped and spaced on 3/4" (19) centers. The frame is to be constructed from heavy gauge extruded aluminum and have reinforced mitered corners. The finish shall be AW Appliance White (optional finishes are available).(Optional) An opposed blade damper, constructed of heavy gauge corrosion-resistant steel (aluminum is optional) and operable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2006.  |

**Models 61DV(-O), 61DH(-O)**

**STEEL SUPPLY GRILLES AND REGISTERS – DOUBLE DEFLECTION**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install **Nailor Model** (select one) **61DV** or **61DH Double Deflection Supply Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall have a dual set of streamlined shaped, roll-formed, corrosion-resistant steel blades that are adjustable, and spaced on 3/4" (19) centers. The frame is to be constructed from roll-formed, corrosion-resistant steel and have reinforced mitered corners. The finish shall be AW Appliance White (optional finishes are available).(Optional) An opposed blade damper, constructed of heavy gauge corrosion-resistant steel and operable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2006. |

**Models 61SV(-O), 61SH(-O)**

**STEEL SUPPLY GRILLES AND REGISTERS – SINGLE DEFLECTION**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install **Nailor Model** (select one) **61SV** or **61SH Single Deflection Supply Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall have a single set of streamlined shaped, roll-formed, corrosion-resistant steel blades that are adjustable, and spaced on 3/4" (19) centers. The frame is to be constructed from roll-formed, corrosion-resistant steel and have reinforced mitered corners. The finish shall be AW Appliance White (optional finishes are available).(Optional) An opposed blade damper, constructed of heavy gauge corrosion-resistant steel and operable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRA Standard 70 – 2006. |

**Models 67DV(-O), 67DH(-O)**

**STAINLESS STEEL SUPPLY GRILLES AND REGISTERS – DOUBLE DEFLECTION**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install **Nailor Model** (select one) **67DV** or **67DH Double Deflection Supply Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall be constructed entirely from 304 stainless steel (316 optional) and have a dual set of streamlined shaped roll-formed adjustable blades that are spaced on 3/4" (19) centers. The frames shall be constructed of heavy gauge stainless steel and have reinforced mitered corners. All exposed surfaces shall have a #4 Brushed Satin Polished finish.(Optional) A stainless steel opposed blade damper adjustable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2006. |

**Models 67SV(-O), 67SH(-O)**

**STAINLESS STEEL SUPPLY GRILLES AND REGISTERS – SINGLE DEFLECTION**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install **Nailor Model** (select one) **67SV** or **67SH Single Deflection Supply Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall be constructed entirely from 304 stainless steel (316 optional) and have a single set of streamlined shaped roll-formed adjustable blades that are spaced on 3/4" (19) centers. The frames shall be constructed of heavy gauge stainless steel and have reinforced mitered corners. All exposed surfaces shall have a #4 Brushed Satin Polished finish.(Optional) A stainless steel opposed blade damper adjustable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2006. |