HOW TO SPECIFY

‘N SLOT’ PREMIUM PERFORMANCE PLENUM SLOT DIFFUSER - HORIZONTAL DISCHARGE, SUPPLY

Models 59N, 59NI

SUGGESTED SPECIFICATION: Furnish and install Nailor Model (select one) 59N or 59NI Horizontal Discharge Plenum Slot Supply Diffusers of the sizes and capacities as shown on the plans and air distribution schedules. The plenum shall be manufactured from corrosion-resistant steel and include a side inlet for connection to the duct. The plenum shall have an extruded aluminum fixed pattern controller within a 3/4" (19) slot. The plenum diffuser shall be supplied in nominal standard lengths of 24", 36", 48" and 60" (600, 900, 1200 and 1500) to suit a standard Lay-in T-Bar ceiling grid. The pattern controller and all exposed edges shall have a BK Black finish. Model 59NI shall be lined internally with insulation. The manufacturer shall provide published performance data for the plenum slot diffuser, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2023.

Models 59NR, 59NRI

‘N SLOT’ PREMIUM PERFORMANCE PLENUM SLOT DIFFUSER - HORIZONTAL DISCHARGE, SUPPLY/RETURN

SUGGESTED SPECIFICATION: Furnish and install Nailor Model (select one) 59NR or 59NRI Horizontal Discharge Plenum Slot Supply/Return Diffusers of the sizes and capacities as shown on the plans and air distribution schedules. The plenum shall be manufactured from corrosion- resistant steel and incorporate a supply air and return air section. The supply plenum shall have an extruded aluminum fixed pattern controller within a 3/4" (19) slot and a side inlet for connection to the supply air duct. The return air section shall have a rectangular return opening on the side that functions as a light shield (top return opening is optional). The plenum diffuser shall be available in nominal standard lengths of 24", 36", 48" and 60" (600, 900, 1200 and 1500) to suit a standard Lay-in T-Bar ceiling grid. The pattern controller and all exposed edges shall have a BK Black finish. Model 59NRI shall be lined internally with insulation. The manufacturer shall provide published performance data for the plenum slot diffuser, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2023.

Models 59ND, 59NDI

‘N SLOT’ PREMIUM PERFORMANCE PLENUM SLOT DIFFUSER – HORIZONTAL/VERTICAL DISCHARGE, SUPPLY

SUGGESTED SPECIFICATION: Furnish and install Nailor Model (select one) 59ND or 59NDI Horizontal/Vertical Discharge Plenum Slot Supply Diffusers of the sizes and capacities as shown on the plans and air distribution schedules. The plenum shall be manufactured from corrosion resistant steel and include a side inlet for connection to the duct. The plenum shall have a central vertical down-blow section that has two hinged pattern controllers within a 1 5/8" (41) slot. The plenum diffuser shall be available in nominal standard lengths of 24", 36", 48" and 60" (600, 900, 1200 and 1500) to suit a standard Lay-in T-Bar ceiling grid. The pattern controller and all exposed edges shall have a BK Black finish. Model 59NDI shall be lined internally with insulation. The manufacturer shall provide published performance data for the plenum slot diffuser, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2023.

Models 59NDR, 59NDRI

‘N SLOT’ PREMIUM PERFORMANCE PLENUM SLOT DIFFUSER – HORIZONTAL/VERTICAL DISCHARGE, SUPPLY/RETURN

SUGGESTED SPECIFICATION: Furnish and install Nailor Model (select one) 59NDR or 59NDRI Horizontal/Vertical Discharge Plenum Slot Supply/Return Diffusers of the sizes and capacities as shown on the plans and air distribution schedules. The plenum shall be manufactured from corrosion-resistant steel and incorporate a supply air and integral return air section. The supply plenum shall have a central vertical down-blow section that has two hinged pattern controllers within a 1 5/8" (41) slot opening, the end sections shall incorporate an extruded aluminum fixed horizontal pattern controller within a 3/4" (19) slot. The supply plenum shall include a side inlet for connection to the duct. The return air plenum shall have a rectangular return opening on the side that also functions as a light shield (top return opening is optional). The plenum diffuser shall be available in nominal standard lengths of 24", 36", 48" and 60" (600, 900, 1200 and 1500) to suit a standard Lay-in T-Bar ceiling grid. The pattern controllers and all exposed edges shall have a BK Black finish. Model 59NDRI shall be lined internally with insulation. The manufacturer shall provide published performance data for the plenum slot diffuser, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2023.

Models 59BS, 59BSI

‘BS’ SERIES PREMIUM PERFORMANCE PLENUM SLOT DIFFUSER – ADJUSTABLE VERTICAL DISCHARGE, SUPPLY

SUGGESTED SPECIFICATION: Furnish and install Nailor Model (select one) 59BS or 59BSI Adjustable Vertical Discharge Plenum Slot Supply Diffusers of the sizes and capacities as shown on the plans and air distribution schedules. The plenum shall be manufactured from corrosion- resistant steel and include a side inlet for connection to the duct. The plenum shall have an extruded aluminum adjustable pattern controller within a 1 3/4" (44) opening. The plenum diffuser shall be supplied in nominal standard lengths of 24", 36", 48" and 60" (600, 900, 1200 and 1500) to suit a standard Lay-in T-Bar ceiling grid. The pattern controller and all exposed edges shall have a BK Black finish. Model 59BSI shall be lined internally with insulation. The manufacturer shall provide published performance data for the plenum slot diffuser, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2023.

Models 59BSR, 59BSRI

‘BS’ SERIES PREMIUM PERFORMANCE PLENUM SLOT DIFFUSER – ADJUSTABLE VERTICAL DISCHARGE, SUPPLY/RETURN

SUGGESTED SPECIFICATION: Furnish and install Nailor Model (select one) 59BSR or 59BSRI Vertical Discharge Plenum Slot Supply/Return Diffusers of the sizes and capacities as shown on the plans and air distribution schedules. The plenum shall be manufactured from corrosion- resistant steel and incorporate a supply air and return air section. The supply plenum shall have an extruded aluminum adjustable pattern controller within a 1 3/4" (44) opening and a side inlet for connection to the supply air duct. The return air plenum shall have a rectangular return opening on the side that also functions as a light shield (top return opening is optional). The plenum diffuser shall be available in nominal standard lengths of 24", 36", 48" and 60" (600, 900, 1200 and 1500) to suit a standard Lay-in T-Bar ceiling grid. The pattern controllers and all exposed edges shall have a BK Black finish. Model 59BSRI shall be lined internally with insulation. The manufacturer shall provide published performance data for the plenum slot diffuser, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2023.