
PLENUM ACCESS DOORS


HOW TO SPECIFY

MODEL 0840-6
PLENUM ACCESS DOOR

	SUGGESTED SPECIFICATION:
Provide and install as shown on plans and/or schedules, plenum access doors as manufactured by Nailor Industries, Inc., which meet the following criteria: Access doors shall meet British Standard DW144 Class C for leakage. Manufacturer shall submit leakage data tested to minimum of 8 in. w.g. (2 kPa). Frame shall be of oval design, constructed of die-formed 22 ga. (0.85) galvanized steel.
Door shall constructed of double skin die-formed 22 ga. (0.85) galvanized steel with 1" (25) insulation fully enclosed within the door panel. Door shall be attached to frame with continuous plated steel piano hinge and shall close securely by means of two die-cast closure handles. Bulb type seal shall be integrally fastened to door for positive seal. Standard of acceptance shall be Nailor Industries Model 0840-6.




MODELS: 0850-2L, 0850-2R, 0855-2L & 0855-2R
THERMAL BREAK PLENUM ACCESS DOORS

	[bookmark: _GoBack]SUGGESTED SPECIFICATION:
Provide and install as shown on plans and/or schedules, thermal break plenum access doors as manufactured by Nailor Industries, Inc., which meet the following criteria: Frames shall be extruded aluminum with mitered corner construction. Door panels shall be constructed of 20 ga. (1.0) galvanized steel. Insulation between door panels shall be 3 lb. density. Thermal isolation shall be achieved utilizing pour-and-debridging technology and each door shall be complete with double gaskets assuring low leakage performance.
Door shall be attached to frame with continuous stainless steel piano type hinge and shall close securely by means of die cast closure handles. 1. Out-swing (negative pressure) operation. Standard of acceptance shall be Nailor Industries Model (specifier to select) 0850-2L with left hand hinge or 0850-2R with right hand hinge or 2. In-swing (positive pressure) operation. Standard of acceptance shall be Nailor Industries Model (specifier to select) 0855-2L with left hand hinge or 0855-2R with right hand hinge.



