
POSITIVE PRESSURE ACCESS DOORS


HOW TO SPECIFY

MODEL: 0800-5
POSITIVE PRESSURE ACCESS DOOR

	[bookmark: _GoBack]SUGGESTED SPECIFICATION:
Provide and install as shown on plans and/or schedules and at each fire damper location, duct access doors as manufactured by Nailor Industries, Inc., which meet the following criteria: Access doors shall meet British Standard DW144 Class C for leakage.
Manufacturer shall submit leakage data tested to minimum of 8 in. w.g. (2 kPa). Frame shall be of oval design, die-formed of minimum 22 ga. (0.85) galvanized steel with 3/16" (5) dia. pre-punched mounting holes. Door shall be constructed of double skin die-formed 22 ga. (0.85) galvanized steel with 1" (25) insulation fully enclosed within the door panel. Door shall be complete with safety handles, quantity dependent on overall size, for secure and controlled opening. Door shall be secured with plated steel wing nut fasteners, with bulb type seal integrally fastened to door providing positive seal. Standard of acceptance shall be Nailor Industries Model 0800-5.



