
ROUND DUCT ACCESS DOORS


HOW TO SPECIFY

MODEL: 0890
LOW PRESSURE ROUND DUCT ACCESS DOOR

	SUGGESTED SPECIFICATION:
Provide and install as shown on plans and/or schedules and at each fire damper location, low pressure duct access doors for round duct as manufactured by Nailor Industries, Inc., which meet the following criteria: Door shall be formed to circumference of duct, constructed of 16 ga. (1.6) galvanized steel with a hinge and zinc plated strikes and catches for secure closing. Door shall be complete with full gasketing to minimize leakage. Standard of acceptance shall be Nailor Industries Model 0890.




MODEL: 0895
HIGH PRESSURE TURRET ROUND DUCT ACCESS DOOR

	[bookmark: _GoBack]SUGGESTED SPECIFICATION:
Provide and install as shown on plans and/or schedules and at each fire damper location, high pressure duct access doors for round duct as manufactured by Nailor Industries, Inc., which meet the following criteria: Access doors shall meet British Standard DW144 Class C for leakage. Manufacturer shall submit leakage data tested to minimum of 8 in. w.g. (2 kPa). Door assembly shall be factory installed and caulked onto a 16 ga. (1.6) galvanized steel welded turret and saddle, formed to match duct circumference. Door frame shall be of oval design, constructed of die-formed 22 ga. (0.85) galvanized steel. Door shall be constructed of double skin die-formed 22 ga. (0.85) galvanized steel 1" (25) insulation fully enclosed within door panels. Bulb type seal shall be integrally fastened to door for positive seal. Standard of acceptance shall be Nailor Industries Model 0895.



