


FIRE RATED & UNIVERSAL ACCESS DOORS


HOW TO SPECIFY

MODEL: 0900-1
FIRE RATED ACCESS DOOR

	SUGGESTED SPECIFICATION:
Provide and install as shown on plans and/or schedules and at each fire damper location, fire rated access doors as manufactured by Nailor Industries, Inc., which meet the following criteria: Access doors shall be approved by Underwriters Laboratories for 1 1/2 hours, with 250°F (121°C) max. temperature rise 'B' Label rating in walls. Access doors shall also be approved by Warnock Hersey for 2 hours in ceilings and 3 hours in walls. Frame shall be constructed of 16 ga. (1.6) corrosion resistant steel. Door panel shall be constructed of 20 ga. (1.0) corrosion resistant steel and shall be filled with minimum 2" (51) thick mineral insulation to reduce heat and sound transfer. Door and latch shall be self-closing. Finish shall be prime coat. Standard of acceptance shall be Nailor Industries Model Series 0900-1
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MODEL 0900-2
UNIVERSAL ACCESS DOOR

	SUGGESTED SPECIFICATION:
Provide and install as shown on plans and/or schedules, universal access doors for wall or ceiling mount as manufactured by Nailor Industries, Inc., which meet the following criteria:. Frame shall be constructed of 16 ga. (1.6) corrosion resistant steel with rounded corners and 3/16" (5) dia. pre-punched mounting holes. Door shall be constructed of 16 ga. (1.6) corrosion resistant steel with concealed hinges, and shall close flush with face of frame. Door latch shall be slotted screwdriver operated. Finish shall be prime coat suitable for field painting to match building interior. Standard of acceptance shall be Nailor Industries Model Series 0900-2..






