CEILING DAMPERS • SQUARE/RECTANGULAR, ROUND



HOW TO SPECIFY

MODELS: 0716, 0716-4, 0722, 0722-SE AND 0722-LE
CEILING DAMPERS

	SUGGESTED SPECIFICATION:
Provide and install, as shown on plans and/or schedules, ceiling dampers as manufactured by Nailor Industries, Inc., which meet the following criteria: Ceiling dampers shall be UL Classified for use in all restrained and unrestrained UL Listed ceiling assemblies with fire resistance ratings of 3 hours or less. Dampers shall be tested and manufactured in accordance with UL 555C Standard for Ceiling Dampers and shall bear a UL label identifying the same.
Frame and blade shall be constructed of 22 ga. (0.85) galvanized steel. Blade insulation shall be non-asbestos UL Classified where required, as determined by overall damper size. Each ceiling damper shall be held open with a (specifier to select) 212°F (100°C) or 165°F (74°C) UL Listed fusible link. Ceiling dampers shall ship with and be installed in accordance to manufacturer’s UL approved installation instructions. Information submitted for approval shall include same UL installation instructions.
[bookmark: _GoBack]Standard of acceptance shall be Nailor Industries (specifier to select) Model 0716 for square or rectangular applications or Model 0716-4 low profile for square or rectangular applications with limited space or Model 0722 for round applications.
(Specifier to select, if required) Model 0722-SE short top extension or Model 0722-LE long top extension, as deemed suitable by space above ceiling, to ensure flex duct does not interfere with blade closure.



