**HOW TO SPECIFY**

**Model 51PR(-O)**

**ALUMINUM PERFORATED RETURN GRILLES AND REGISTERS**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install **Nailor Model 51PR Perforated Return Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall have an aluminum perforated core with 3/16" (5) dia. holes on 1/4" (6) staggered centers, providing 51% free area. The frame is to be constructed from extruded aluminum and have reinforced mitered corners. The finish shall be AW Appliance White (optional finishes are available).(Optional) An opposed blade damper, constructed of heavy gauge corrosion-resistant steel (aluminum is optional) and operable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2006.. |

**Model 61PR(-O)**

**STEEL PERFORATED RETURN GRILLES AND REGISTERS**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install **Nailor Model 61PR Perforated Return Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall have a corrosion-resistant steel perforated core with 3/16" (5) dia. holes on 1/4" (6) staggered centers, providing 51% free area. The frame is to be constructed from roll-formed corrosion-resistant steel and have reinforced mitered corners. The finish shall be AW Appliance White (optional finishes are available).(Optional) An opposed blade damper, constructed of heavy gauge corrosion-resistant steel and operable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2006. |

**Model 67PR(-O)**

**STAINLESS STEEL PERFORATED RETURN GRILLES AND REGISTERS**

|  |
| --- |
| **SUGGESTED SPECIFICATION:**Furnish and install **Nailor Model 67PR Perforated Return Grilles** of the type and size as shown on the plans and air distribution schedules. The grilles shall be constructed entirely from 304 stainless steel (316 optional). The perforated core shall have 3/16"(5) dia. perforated holes on 1/4" (6) staggered centers, providing 51% free area. The frames shall be constructed of heavy gauge stainless steel and have reinforced mitered corners. All exposed surfaces shall have a #4 Brushed Satin Polished finish (optional AW Appliance White finish).(Optional) A stainless steel opposed blade damper adjustable from the face of the grille, shall be provided with all units.The manufacturer shall provide published performance data for the grille, which shall be tested in accordance with ANSI/ASHRAE Standard 70 – 2006. |